## pxm2k-modbus-uid-0
Parameter Name | Display Name | Base Address (1-based) | Discrete | Units | Type | Size (bytes) | Is Timestamp | Bit Offset | Swap Bytes | Swap Words | Divider | Multiplier | Date Spec | Alarm On False | Writable | Value | Possible Values | Description
VendorName/Value | Vendor Name | 1033 | No | no-units | STRING | 64 | No |  | No | No |  |  |  |  | No | Eaton Corporation |  | Name of the device manufacturer.
ModelName/Value | Model Name | 1065 | No | no-units | STRING | 64 | No |  | No | No |  |  |  |  | No | PXM2250 |  | Model Name of the device.
iDisplayName/Value | Display Name | 1097 | No | no-units | STRING | 64 | No |  | No | No |  |  |  |  | Yes | Power Xpert 2250 Meter |  | Display Name of the device.
iDeviceType/Value | Device Type | 1129 | No | no-units | STRING | 64 | No |  | No | No |  |  |  |  | No | Meter |  | Device Type of the device.
SerialNumber/Value | Serial Number | 1277 | No | no-units | STRING | 64 | No |  | No | No |  |  |  |  | No | 186738639 |  | Serial number of the device.
SoftwareVersion/Value | Software Version | 2109 | No | no-units | STRING | 48 | No |  | No | No |  |  |  |  | No | 32 |  | Software version of the device.
iDeviceVARating/Value | VA Rating | 1352 | No | volt-amperes | UINT | 4 | No |  | No | No |  |  |  |  | No | 8640000 |  | Nominal VA rating of the device.
iDeviceVoltsRating/Value | Nominal Voltage | 1356 | No | volts | UINT | 4 | No |  | No | No |  |  |  |  | Yes | 2400 |  | Nominal voltage rating of the device.
iNumPhases/Value | Phases to Display on Meter Front | 1362 | No | no-units | UINT | 2 | No |  | No | No |  |  |  |  | Yes | 3 | 1;2;3 | Number of phases the device supports.
iFieldReplaceableUnit/Value | Field Replaceable Unit | 1606 | No | no-units | UINT | 2 | No |  | No | No |  |  |  |  | Yes | TRUE | true;false | Is the device field replaceable?
iNominalFrequency/Value | Nominal Frequency | 1669 | No | hertz | UINT | 2 | No |  | No | No |  |  |  |  | No | 60 |  | Nominal frequency of the device.
iDeviceAmpsRating/Value | Output Current Rating | 1811 | No | amperes | UINT | 2 | No |  | No | No |  |  |  |  | Yes | 1200 |  | Output Current Rating.
sStatus/Value | Status | 3001 | No | no-units | UINT | 2 | No |  | No | No |  |  |  |  | No | 1 | Off(0);Normal(1);Limp mode(2);Warmup(3);Unknown(4);Unknown2(5);Booting up(6);Boot up(7) | Indicates the current operating status of the device.
mACVAB/Value | Vab | 4003 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to B RMS Voltage.
mACVBC/Value | Vbc | 4005 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to C RMS Voltage.
mACVCA/Value | Vca | 4007 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to A RMS Voltage.
mACVavgLL/Value | V(L-L) Average | 4009 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Line RMS Voltage.
mACVAN/Value | Van | 4011 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to Neutral RMS Voltage.
mACVBN/Value | Vbn | 4013 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to Neutral RMS Voltage.
mACVCN/Value | Vcn | 4015 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to Neutral RMS Voltage.
mACVavgLN/Value | V(L-N) Average | 4017 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Neutral RMS Voltage.
mPosSeqV/Value | V(Positive Sequence) Magnitude | 4184 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Posive Sequence Symmetric Voltage.
mNegSeqV/Value | V(Negative Sequence) Magnitude | 4188 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Negative Sequence Symmetric Voltage.
mZeroSeqV/Value | V(Zero Sequence) Magnitude | 4192 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Zero Sequence Symmetric Voltage.
mPercentVoltageUnbalance/Value | Percent Voltage unbalance Negative Sequence | 4484 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Voltage Unbalance.
mPhaseAngleVab/Value | Phase Angle Vab | 4498 | No | degrees-phase | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Voltage AB Phase Angle.
mPhaseAngleVbc/Value | Phase Angle Vbc | 4500 | No | degrees-phase | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Voltage BC Phase Angle.
mPhaseAngleVca/Value | Phase Angle Vca | 4502 | No | degrees-phase | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Voltage CA Phase Angle.
mACIA/Value | Ia | 5003 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A RMS Current.
mACIB/Value | Ib | 5005 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B RMS Current.
mACIC/Value | Ic | 5007 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C RMS Current.
mACIN/Value | In | 5011 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Neutral RMS Current.
mACIavg/Value | Iavg | 5013 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Phase RMS Current.
mDemandIa/Value | Demand Ia | 5251 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Ia.
mDemandIb/Value | Demand Ib | 5253 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0.019376 |  | Demand Ib.
mDemandIc/Value | Demand Ic | 5255 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Ic.
mDemandIn/Value | Demand In | 5259 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand In.
mACIAPeakDemand/Value | Peak Demand Ia | 5015 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 580.752 |  | Phase A peak demand current.
mACIBPeakDemand/Value | Peak Demand Ib | 5017 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 581.327 |  | Phase B peak demand current.
mACICPeakDemand/Value | Peak Demand Ic | 5019 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 572.06 |  | Phase C peak demand current.
mDemandInPeak/Value | Peak Demand In | 5263 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 38.7683 |  | Peak Demand In.
mPhaseAngleIa/Value | Phase Angle Ia | 5339 | No | degrees-phase | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A Current Phase Angle.
mPhaseAngleIb/Value | Phase Angle Ib | 5341 | No | degrees-phase | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B Current Phase Angle.
mPhaseAngleIc/Value | Phase Angle Ic | 5343 | No | degrees-phase | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C Current Phase Angle.
mACIAPeakDemandTime/Value | Time of Peak Demand Ia | 5547 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2016-11-29T00:00:00Z |  | Time of Phase A peak demand current.
mACIBPeakDemandTime/Value | Time of Peak Demand Ib | 5550 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2017-12-08T03:30:00Z |  | Time of Phase B peak demand current.
mACICPeakDemandTime/Value | Time of Peak Demand Ic | 5553 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2016-11-29T00:00:00Z |  | Time of Phase C peak demand current.
mACINPeakDemandTime/Value | Time of Peak Demand In | 5556 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2018-01-17T14:15:00Z |  | Time of Neutral peak demand current.
mWA/Value | Real Power Phase A | 6001 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A real power.
mWB/Value | Real Power Phase B | 6003 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B real power.
mWC/Value | Real Power Phase C | 6005 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C real power.
mWtotal/Value | Real Power | 6007 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase real power.
mVAA/Value | Apparent Power Phase A | 6065 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A VA.
mVAB/Value | Apparent Power Phase B | 6067 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B VA.
mVAC/Value | Apparent Power Phase C | 6069 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C VA.
mVAtotal/Value | Apparent Power | 6071 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase VA.
mVarA/Value | Reactive Power Phase A | 6129 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A reactive power.
mVarB/Value | Reactive Power Phase B | 6131 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B reactive power.
mVarC/Value | Reactive Power Phase C | 6133 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C reactive power.
mVARtotal/Value | Reactive Power | 6135 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase reactive power.
mPercentUnbalance/Value | Percent Current Unbalance | 6193 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Phase Unbalance.
mPFapparentA/Value | PF App Phase A | 6213 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A apparent power factor.
mPFapparentB/Value | PF App Phase B | 6215 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B apparent power factor.
mPFapparentC/Value | PF App Phase C | 6217 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C apparent power factor.
mPFapparentTotal/Value | PF Apparent | 6221 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase apparent power factor.
mPFapparentTotal5MinIntAvg/Value | PF App Total Interval Avg | 6317 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1 |  | 3 Phase apparent power factor.
mForwardEnergy/Value | Forward Real Energy | 7005 | No | watt-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Forward Energy. (delivered).
mReverseEnergy/Value | Reverse Real Energy | 7007 | No | watt-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Reverse Energy. (received).
mTotalEnergy/Value | Total Real Energy | 7680 | No | watt-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Total Energy. (forward+reverse; or delivered+received).
mNetEnergy/Value | Net Real Energy | 7009 | No | watt-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Net Energy. (forward-reverse; or delivered-received).
mVAh/Value | Apparent Energy | 7017 | No | volt-ampere-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | VA hours.
mLeadingVARh/Value | Leading Reactive Energy | 7011 | No | volt-ampere-reactive-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Leading vahours.
mLaggingVARh/Value | Lagging Reactive Energy | 7013 | No | volt-ampere-reactive-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Lagging varhours.
mTotalVARh/Value | Total Reactive Energy | 7629 | No | volt-ampere-reactive-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Total varhours. (lag+lead; or delivered+received).
mNetVARh/Value | Net Reactive Energy | 7015 | No | volt-ampere-reactive-hours | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Net varhours. (lag-lead; or delivered-received).
mDemandVAs/Value | Demand VAs | 7388 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand VAs.
mPeakDemandVAs/Value | Peak Demand VAs | 7390 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 2404560 |  | Peak Demand VAs.
mTimeDatePeakDemandVAs/Value | Peak Demand VAs Time | 7392 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2018-03-21T03:15:00Z |  | Peak Demand VAs Time.
mDemandForwardWatts/Value | Demand Forward Watts | 7221 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Forward Watts.
mPeakDemandForwardWatts/Value | Peak Demand Forward Watts | 7223 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 17379.7 |  | Peak Demand Forward Watts.
mTimeDatePeakDemandForwardWatts/Value | Peak Demand Forward Watts Time | 7225 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2017-10-28T08:15:00Z |  | Peak Demand Forward Watts Time.
mDemandReverseWatts/Value | Demand Reverse Watts | 7263 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Reverse Watts.
mPeakDemandReverseWatts/Value | Peak Demand Reverse Watts | 7265 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | -2402635 |  | Peak Demand Reverse Watts.
mTimeDatePeakDemandReverseWatts/Value | Peak Demand Reverse Watts Time | 7267 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2018-03-21T03:15:00Z |  | Peak Demand Reverse Watts Time.
mDemandLaggingVARs/Value | Demand Lagging VARs | 7304 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Lagging VARs.
mPeakDemandLaggingVARs/Value | Peak Demand Lagging VARs | 7306 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 632556 |  | Peak Demand Lagging VARs.
mTimeDatePeakDemandLaggingVARs/Value | Peak Demand Lagging VARs Time | 7308 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2017-06-01T20:30:00Z |  | Peak Demand Lagging VARs Time.
mDemandLeadingVARs/Value | Demand Leading VARs | 7346 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Leading VARs.
mPeakDemandLeadingVARs/Value | Peak Demand Leading VARs | 7348 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | -43152.7 |  | Peak Demand Leading VARs.
mTimeDatePeakDemandLeadingVARs/Value | Peak Demand Leading VARs Time | 7350 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2017-03-17T20:15:00Z |  | Peak Demand Leading VARs Time.
mDemandSumWatts/Value | Demand Sum Watts | 7026 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Sum Watts.
mDemandNetWatts/Value | Demand Net Watts | 7028 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Net Watts.
mDemandSumVARs/Value | Demand Sum VARs | 7032 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Sum VARs.
mDemandNetVARs/Value | Demand Net VARs | 7034 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Net VARs.
mTimeLastDemand/Value | Time Last Demand Window | 7038 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2022-06-07T18:30:00Z |  | Time Last demand window .
mDemandType/Value | Demand Type | 7166 | No | no-units | UINT | 2 | No |  | No | No |  |  |  |  | Yes | 1 | Fixed(1);Sliding(2);Sync(3);Unknown(4);Derived(5) | Demand Type ( Fixed; Sliding; External_sync).
mTotalDemandInterval/Value | Demand Interval | 7167 | No | minutes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 15 | 5;10;15;20;30;45;60 | Total Demand Interval.
mDemandSubinterval/Value | Demand Subinterval | 7169 | No | minutes | FLOAT | 4 | No |  | No | No |  |  |  |  | Yes | 15 | 5;15;30;60 | Demand subinterval.
mIntDemandForwardWatts/Value | Interval Demand Forward Watts | 7171 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Forward Watts for Profile.
mIntDemandReverseWatts/Value | Interval Demand Reverse Watts | 7173 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Reverse Watts for Profile.
mIntDemandLaggingVARs/Value | Interval Demand Lagging VARs | 7175 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Lagging VARs for Profile.
mIntDemandLeadingVARs/Value | Interval Demand Leading VARs | 7177 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Leading VARs for Profile.
mIntDemandVAs/Value | Interval Demand VAs | 7179 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand VAs for Profile.
mDemandAmpsAvg/Value | Demand Current (3 Phase Avg) | 7430 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0.0064586 |  | Demand Current (3 Phase Avg).
mPeakDemandAmpsAvg/Value | Peak Demand Amps Avg | 7432 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0.0066169 |  | Peak Demand Amps Avg.
mPeakDemandSumWatts/Value | Peak Demand Sum Watts | 7684 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Peak Demand Sum Watts.
mPeakDemandNetWatts/Value | Peak Demand Net Watts | 7689 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Peak Demand Net Watts.
mPeakDemandSumVARs/Value | Peak Demand Sum VARs | 7694 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Peak Demand Sum VARs.
mPeakDemandNetVARs/Value | Peak Demand Net VARs | 7699 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Peak Demand Net VARs.
mTimePeakDemandNetVARs/Value | Time Peak Demand Net VARs | 7701 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2022-06-07T18:32:48Z |  | Time Peak Demand Net VARs.
mIntDemandSumWatts/Value | Interval Demand Sum Watts | 7708 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Sum Watts.
mIntDemandSumVARs/Value | Interval Demand Sum VARs | 7710 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Sum VARs.
mPFatPeakDemandForwardWatts/Value | Power Factor at Peak Demand Forward Watts | 7832 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1 |  | Power Factor at Peak Demand Forward Watts.
mPFatPeakDemandReverseWatts/Value | Power Factor at Peak Demand Reverse Watts | 7842 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1 |  | Power Factor at Peak Demand Reverse Watts.
mPFatPeakDemandVA/Value | Power Factor at Peak Demand VA | 7850 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1 |  | Power Factor at Peak Demand VA.
mPFatPeakDemandLeadingVars/Value | Power Factor at Peak Demand Leading Vars | 7852 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1 |  | Power Factor at Peak Demand Leading Vars.
mPFatPeakDemandLaggingVars/Value | Power Factor at Peak Demand Lagging Vars | 7854 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1 |  | Power Factor at Peak Demand Lagging Vars.
mIntDemandNetWatts/Value | Interval Demand Net Watts | 7856 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Net Watts.
mIntDemandNetVARs/Value | Interval Demand Net VARs | 7858 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Interval Demand Net VARs.
mFreq/Value | Frequency | 11001 | No | hertz | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Frequency.
mLastStartTime/Value | Time of Last Start | 12235 | No | no-units | DATE | 6 | No |  | No | No |  |  | ymdHMS |  | No | 2022-06-07T18:30:42Z |  | Time of Last Start.
EventListItem1/ID | EventListItem1 Event ID | 46001 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem1/Time | EventListItem1 Timestamp | 46003 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem1/Cause | EventListItem1 Cause | 46009 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem1/Param | EventListItem1 (Unused) | 46010 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem1/WaveformID | EventListItem1 Waveform File ID | 46012 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem2/ID | EventListItem2 Event ID | 46014 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem2/Time | EventListItem2 Timestamp | 46016 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem2/Cause | EventListItem2 Cause | 46022 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem2/Param | EventListItem2 (Unused) | 46023 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem2/WaveformID | EventListItem2 Waveform File ID | 46025 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem3/ID | EventListItem3 Event ID | 46027 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem3/Time | EventListItem3 Timestamp | 46029 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem3/Cause | EventListItem3 Cause | 46035 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem3/Param | EventListItem3 (Unused) | 46036 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem3/WaveformID | EventListItem3 Waveform File ID | 46038 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem4/ID | EventListItem4 Event ID | 46040 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem4/Time | EventListItem4 Timestamp | 46042 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem4/Cause | EventListItem4 Cause | 46048 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem4/Param | EventListItem4 (Unused) | 46049 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem4/WaveformID | EventListItem4 Waveform File ID | 46051 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem5/ID | EventListItem5 Event ID | 46053 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem5/Time | EventListItem5 Timestamp | 46055 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem5/Cause | EventListItem5 Cause | 46061 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem5/Param | EventListItem5 (Unused) | 46062 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem5/WaveformID | EventListItem5 Waveform File ID | 46064 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem6/ID | EventListItem6 Event ID | 46066 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem6/Time | EventListItem6 Timestamp | 46068 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem6/Cause | EventListItem6 Cause | 46074 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem6/Param | EventListItem6 (Unused) | 46075 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem6/WaveformID | EventListItem6 Waveform File ID | 46077 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem7/ID | EventListItem7 Event ID | 46079 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem7/Time | EventListItem7 Timestamp | 46081 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem7/Cause | EventListItem7 Cause | 46087 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem7/Param | EventListItem7 (Unused) | 46088 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem7/WaveformID | EventListItem7 Waveform File ID | 46090 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem8/ID | EventListItem8 Event ID | 46092 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem8/Time | EventListItem8 Timestamp | 46094 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem8/Cause | EventListItem8 Cause | 46100 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem8/Param | EventListItem8 (Unused) | 46101 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem8/WaveformID | EventListItem8 Waveform File ID | 46103 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem9/ID | EventListItem9 Event ID | 46105 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem9/Time | EventListItem9 Timestamp | 46107 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem9/Cause | EventListItem9 Cause | 46113 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem9/Param | EventListItem9 (Unused) | 46114 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem9/WaveformID | EventListItem9 Waveform File ID | 46116 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem10/ID | EventListItem10 Event ID | 46118 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem10/Time | EventListItem10 Timestamp | 46120 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem10/Cause | EventListItem10 Cause | 46126 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem10/Param | EventListItem10 (Unused) | 46127 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem10/WaveformID | EventListItem10 Waveform File ID | 46129 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem11/ID | EventListItem11 Event ID | 46131 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem11/Time | EventListItem11 Timestamp | 46133 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem11/Cause | EventListItem11 Cause | 46139 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem11/Param | EventListItem11 (Unused) | 46140 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem11/WaveformID | EventListItem11 Waveform File ID | 46142 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem12/ID | EventListItem12 Event ID | 46144 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem12/Time | EventListItem12 Timestamp | 46146 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem12/Cause | EventListItem12 Cause | 46152 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem12/Param | EventListItem12 (Unused) | 46153 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem12/WaveformID | EventListItem12 Waveform File ID | 46155 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem13/ID | EventListItem13 Event ID | 46157 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem13/Time | EventListItem13 Timestamp | 46159 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem13/Cause | EventListItem13 Cause | 46165 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem13/Param | EventListItem13 (Unused) | 46166 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem13/WaveformID | EventListItem13 Waveform File ID | 46168 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem14/ID | EventListItem14 Event ID | 46170 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem14/Time | EventListItem14 Timestamp | 46172 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem14/Cause | EventListItem14 Cause | 46178 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem14/Param | EventListItem14 (Unused) | 46179 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem14/WaveformID | EventListItem14 Waveform File ID | 46181 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem15/ID | EventListItem15 Event ID | 46183 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem15/Time | EventListItem15 Timestamp | 46185 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem15/Cause | EventListItem15 Cause | 46191 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem15/Param | EventListItem15 (Unused) | 46192 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem15/WaveformID | EventListItem15 Waveform File ID | 46194 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem16/ID | EventListItem16 Event ID | 46196 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem16/Time | EventListItem16 Timestamp | 46198 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem16/Cause | EventListItem16 Cause | 46204 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem16/Param | EventListItem16 (Unused) | 46205 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem16/WaveformID | EventListItem16 Waveform File ID | 46207 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem17/ID | EventListItem17 Event ID | 46209 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem17/Time | EventListItem17 Timestamp | 46211 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem17/Cause | EventListItem17 Cause | 46217 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem17/Param | EventListItem17 (Unused) | 46218 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem17/WaveformID | EventListItem17 Waveform File ID | 46220 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem18/ID | EventListItem18 Event ID | 46222 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem18/Time | EventListItem18 Timestamp | 46224 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem18/Cause | EventListItem18 Cause | 46230 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem18/Param | EventListItem18 (Unused) | 46231 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem18/WaveformID | EventListItem18 Waveform File ID | 46233 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem19/ID | EventListItem19 Event ID | 46235 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem19/Time | EventListItem19 Timestamp | 46237 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem19/Cause | EventListItem19 Cause | 46243 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem19/Param | EventListItem19 (Unused) | 46244 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem19/WaveformID | EventListItem19 Waveform File ID | 46246 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem20/ID | EventListItem20 Event ID | 46248 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
EventListItem20/Time | EventListItem20 Timestamp | 46250 | No |  | DATE | 12 | No |  | No | No |  |  | mmddYYHHMMQQ |  | No
EventListItem20/Cause | EventListItem20 Cause | 46256 | No |  | UINT | 2 | No |  | No | No |  |  |  |  | No
EventListItem20/Param | EventListItem20 (Unused) | 46257 | No |  | FLOAT | 4 | No |  | No | No |  |  |  |  | No
EventListItem20/WaveformID | EventListItem20 Waveform File ID | 46259 | No |  | UINT | 4 | No |  | No | No |  |  |  |  | No
mACVAB/.ValueMin | Vab (minimum value) | 25101 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to B RMS Voltage.
mACVAB/.ValueMin | Vab (minimum value) -- Date | 25103 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase A to B RMS Voltage.
mACVAB/.ValueMax | Vab (maximum value) | 25106 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 2678.91 |  | Phase A to B RMS Voltage.
mACVAB/.ValueMax | Vab (maximum value) -- Date | 25108 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase A to B RMS Voltage.
mACVBC/.ValueMin | Vbc (minimum value) | 25111 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to C RMS Voltage.
mACVBC/.ValueMin | Vbc (minimum value) -- Date | 25113 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase B to C RMS Voltage.
mACVBC/.ValueMax | Vbc (maximum value) | 25116 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 3083.12 |  | Phase B to C RMS Voltage.
mACVBC/.ValueMax | Vbc (maximum value) -- Date | 25118 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase B to C RMS Voltage.
mACVCA/.ValueMin | Vca (minimum value) | 25121 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to A RMS Voltage.
mACVCA/.ValueMin | Vca (minimum value) -- Date | 25123 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase C to A RMS Voltage.
mACVCA/.ValueMax | Vca (maximum value) | 25126 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 2719.53 |  | Phase C to A RMS Voltage.
mACVCA/.ValueMax | Vca (maximum value) -- Date | 25128 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase C to A RMS Voltage.
mACVAN/.ValueMin | Van (minimum value) | 25131 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to Neutral RMS Voltage.
mACVAN/.ValueMin | Van (minimum value) -- Date | 25133 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase A to Neutral RMS Voltage.
mACVAN/.ValueMax | Van (maximum value) | 25136 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1591.51 |  | Phase A to Neutral RMS Voltage.
mACVAN/.ValueMax | Van (maximum value) -- Date | 25138 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase A to Neutral RMS Voltage.
mACVBN/.ValueMin | Vbn (minimum value) | 25141 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to Neutral RMS Voltage.
mACVBN/.ValueMin | Vbn (minimum value) -- Date | 25143 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase B to Neutral RMS Voltage.
mACVBN/.ValueMax | Vbn (maximum value) | 25146 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1666.15 |  | Phase B to Neutral RMS Voltage.
mACVBN/.ValueMax | Vbn (maximum value) -- Date | 25148 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase B to Neutral RMS Voltage.
mACVCN/.ValueMin | Vcn (minimum value) | 25151 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to Neutral RMS Voltage.
mACVCN/.ValueMin | Vcn (minimum value) -- Date | 25153 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase C to Neutral RMS Voltage.
mACVCN/.ValueMax | Vcn (maximum value) | 25156 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 1660.28 |  | Phase C to Neutral RMS Voltage.
mACVCN/.ValueMax | Vcn (maximum value) -- Date | 25158 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase C to Neutral RMS Voltage.
mACIAPeakDemand/Value | Peak Demand Ia -- Date | 25201 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase A peak demand current.
mACIBPeakDemand/Value | Peak Demand Ib -- Date | 25204 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase B peak demand current.
mACICPeakDemand/Value | Peak Demand Ic -- Date | 25207 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Phase C peak demand current.
mDemandInPeak/Value | Peak Demand In -- Date | 25210 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand In.
mPeakDemandAmpsAvg/Value | Peak Demand Amps Avg -- Date | 25213 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Amps Avg.
mPeakDemandForwardWatts/Value | Peak Demand Forward Watts -- Date | 25216 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Forward Watts.
mPeakDemandReverseWatts/Value | Peak Demand Reverse Watts -- Date | 25219 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Reverse Watts.
mPeakDemandLaggingVARs/Value | Peak Demand Lagging VARs -- Date | 25222 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Lagging VARs.
mPeakDemandLeadingVARs/Value | Peak Demand Leading VARs -- Date | 25225 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Leading VARs.
mPeakDemandVAs/Value | Peak Demand VAs -- Date | 25228 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand VAs.
mPeakDemandNetWatts/Value | Peak Demand Net Watts -- Date | 25231 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Net Watts.
mPeakDemandSumWatts/Value | Peak Demand Sum Watts -- Date | 25234 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Sum Watts.
mPeakDemandNetVARs/Value | Peak Demand Net VARs -- Date | 25237 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Net VARs.
mPeakDemandSumVARs/Value | Peak Demand Sum VARs -- Date | 25240 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Peak Demand Sum VARs.
mFreq/.ValueMin | Frequency (minimum value) | 25361 | No | hertz | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Frequency.
mFreq/.ValueMin | Frequency (minimum value) -- Date | 25363 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Frequency.
mFreq/.ValueMax | Frequency (maximum value) | 25366 | No | hertz | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 62.1772 |  | Frequency.
mFreq/.ValueMax | Frequency (maximum value) -- Date | 25368 | No |  | DATE | 6 | Yes |  | No | No |  |  | ymdHMS |  | No |  |  | Frequency.
aEventDescr01/Value | Event 1 (Latest) | 25401 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev1
aEventDescr02/Value | Event 2 | 25526 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev2
aEventDescr03/Value | Event 3 | 25651 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev3
aEventDescr04/Value | Event 4 | 25776 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev4
aEventDescr05/Value | Event 5 | 25901 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev5
aEventDescr06/Value | Event 6 | 26026 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev6
aEventDescr07/Value | Event 7 | 26151 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev7
aEventDescr08/Value | Event 8 | 26276 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev8
aEventDescr09/Value | Event 9 | 26401 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev9
aEventDescr10/Value | Event 10 | 26526 | No |  | STRING | 250 | No |  | No | No |  |  |  |  | No | ev10
mACIA/.ValueIntMin | Ia (5-min interval minimum) | 45301 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A RMS Current.
mACIA/.ValueIntAvg | Ia (5-min interval average) | 45303 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A RMS Current.
mACIA/.ValueIntMax | Ia (5-min interval maximum) | 45305 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A RMS Current.
mACIB/.ValueIntMin | Ib (5-min interval minimum) | 45307 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B RMS Current.
mACIB/.ValueIntAvg | Ib (5-min interval average) | 45309 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B RMS Current.
mACIB/.ValueIntMax | Ib (5-min interval maximum) | 45311 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B RMS Current.
mACIC/.ValueIntMin | Ic (5-min interval minimum) | 45313 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C RMS Current.
mACIC/.ValueIntAvg | Ic (5-min interval average) | 45315 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C RMS Current.
mACIC/.ValueIntMax | Ic (5-min interval maximum) | 45317 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C RMS Current.
mACIN/.ValueIntMin | In (5-min interval minimum) | 45319 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Neutral RMS Current.
mACIN/.ValueIntAvg | In (5-min interval average) | 45321 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Neutral RMS Current.
mACIN/.ValueIntMax | In (5-min interval maximum) | 45323 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Neutral RMS Current.
mACIavg/.ValueIntMin | Iavg (5-min interval minimum) | 45325 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Phase RMS Current.
mACIavg/.ValueIntAvg | Iavg (5-min interval average) | 45327 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Phase RMS Current.
mACIavg/.ValueIntMax | Iavg (5-min interval maximum) | 45329 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Phase RMS Current.
mACVAN/.ValueIntMin | Van (5-min interval minimum) | 45331 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to Neutral RMS Voltage.
mACVAN/.ValueIntAvg | Van (5-min interval average) | 45333 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to Neutral RMS Voltage.
mACVAN/.ValueIntMax | Van (5-min interval maximum) | 45335 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to Neutral RMS Voltage.
mACVBN/.ValueIntMin | Vbn (5-min interval minimum) | 45337 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to Neutral RMS Voltage.
mACVBN/.ValueIntAvg | Vbn (5-min interval average) | 45339 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to Neutral RMS Voltage.
mACVBN/.ValueIntMax | Vbn (5-min interval maximum) | 45341 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to Neutral RMS Voltage.
mACVCN/.ValueIntMin | Vcn (5-min interval minimum) | 45343 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to Neutral RMS Voltage.
mACVCN/.ValueIntAvg | Vcn (5-min interval average) | 45345 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to Neutral RMS Voltage.
mACVCN/.ValueIntMax | Vcn (5-min interval maximum) | 45347 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to Neutral RMS Voltage.
mACVavgLN/.ValueIntMin | V(L-N) Average (5-min interval minimum) | 45349 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Neutral RMS Voltage.
mACVavgLN/.ValueIntAvg | V(L-N) Average (5-min interval average) | 45351 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Neutral RMS Voltage.
mACVavgLN/.ValueIntMax | V(L-N) Average (5-min interval maximum) | 45353 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Neutral RMS Voltage.
mACVAB/.ValueIntMin | Vab (5-min interval minimum) | 45355 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to B RMS Voltage.
mACVAB/.ValueIntAvg | Vab (5-min interval average) | 45357 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to B RMS Voltage.
mACVAB/.ValueIntMax | Vab (5-min interval maximum) | 45359 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A to B RMS Voltage.
mACVBC/.ValueIntMin | Vbc (5-min interval minimum) | 45361 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to C RMS Voltage.
mACVBC/.ValueIntAvg | Vbc (5-min interval average) | 45363 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to C RMS Voltage.
mACVBC/.ValueIntMax | Vbc (5-min interval maximum) | 45365 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B to C RMS Voltage.
mACVCA/.ValueIntMin | Vca (5-min interval minimum) | 45367 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to A RMS Voltage.
mACVCA/.ValueIntAvg | Vca (5-min interval average) | 45369 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to A RMS Voltage.
mACVCA/.ValueIntMax | Vca (5-min interval maximum) | 45371 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C to A RMS Voltage.
mACVavgLL/.ValueIntMin | V(L-L) Average (5-min interval minimum) | 45373 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Line RMS Voltage.
mACVavgLL/.ValueIntAvg | V(L-L) Average (5-min interval average) | 45375 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Line RMS Voltage.
mACVavgLL/.ValueIntMax | V(L-L) Average (5-min interval maximum) | 45377 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Average Line to Line RMS Voltage.
mDemandAmpsAvg/.ValueIntAvg | Demand Current (3 Phase Avg) (5-min interval average) | 45379 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0.0064586 |  | Demand Current (3 Phase Avg).
mDemandForwardWatts/.ValueIntAvg | Demand Forward Watts (5-min interval average) | 45381 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Forward Watts.
mDemandIa/.ValueIntAvg | Demand Ia (5-min interval average) | 45383 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Ia.
mDemandIb/.ValueIntAvg | Demand Ib (5-min interval average) | 45385 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0.019376 |  | Demand Ib.
mDemandIc/.ValueIntAvg | Demand Ic (5-min interval average) | 45387 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Ic.
mDemandIn/.ValueIntAvg | Demand In (5-min interval average) | 45389 | No | amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand In.
mDemandLaggingVARs/.ValueIntAvg | Demand Lagging VARs (5-min interval average) | 45391 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Lagging VARs.
mDemandLeadingVARs/.ValueIntAvg | Demand Leading VARs (5-min interval average) | 45393 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Leading VARs.
mDemandNetVARs/.ValueIntAvg | Demand Net VARs (5-min interval average) | 45395 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Net VARs.
mDemandNetWatts/.ValueIntAvg | Demand Net Watts (5-min interval average) | 45397 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Net Watts.
mDemandReverseWatts/.ValueIntAvg | Demand Reverse Watts (5-min interval average) | 45399 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Reverse Watts.
mDemandSumVARs/.ValueIntAvg | Demand Sum VARs (5-min interval average) | 45401 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Sum VARs.
mDemandSumWatts/.ValueIntAvg | Demand Sum Watts (5-min interval average) | 45403 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand Sum Watts.
mDemandVAs/.ValueIntAvg | Demand VAs (5-min interval average) | 45405 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Demand VAs.
mFreq/.ValueIntMin | Frequency (5-min interval minimum) | 45443 | No | hertz | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Frequency.
mFreq/.ValueIntAvg | Frequency (5-min interval average) | 45445 | No | hertz | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Frequency.
mFreq/.ValueIntMax | Frequency (5-min interval maximum) | 45447 | No | hertz | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Frequency.
mPFapparentA/.ValueIntMin | PF App Phase A (5-min interval minimum) | 45449 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A apparent power factor.
mPFapparentA/.ValueIntAvg | PF App Phase A (5-min interval average) | 45451 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A apparent power factor.
mPFapparentA/.ValueIntMax | PF App Phase A (5-min interval maximum) | 45453 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A apparent power factor.
mPFapparentB/.ValueIntMin | PF App Phase B (5-min interval minimum) | 45455 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B apparent power factor.
mPFapparentB/.ValueIntAvg | PF App Phase B (5-min interval average) | 45457 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B apparent power factor.
mPFapparentB/.ValueIntMax | PF App Phase B (5-min interval maximum) | 45459 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B apparent power factor.
mPFapparentC/.ValueIntMin | PF App Phase C (5-min interval minimum) | 45461 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C apparent power factor.
mPFapparentC/.ValueIntAvg | PF App Phase C (5-min interval average) | 45463 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C apparent power factor.
mPFapparentC/.ValueIntMax | PF App Phase C (5-min interval maximum) | 45465 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C apparent power factor.
mPFapparentTotal/.ValueIntMin | PF Apparent (5-min interval minimum) | 45467 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase apparent power factor.
mPFapparentTotal/.ValueIntAvg | PF Apparent (5-min interval average) | 45469 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase apparent power factor.
mPFapparentTotal/.ValueIntMax | PF Apparent (5-min interval maximum) | 45471 | No | power-factor | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase apparent power factor.
mNegSeqV/.ValueIntMin | V(Negative Sequence) Magnitude (5-min interval minimum) | 45473 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Negative Sequence Symmetric Voltage.
mNegSeqV/.ValueIntAvg | V(Negative Sequence) Magnitude (5-min interval average) | 45475 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Negative Sequence Symmetric Voltage.
mNegSeqV/.ValueIntMax | V(Negative Sequence) Magnitude (5-min interval maximum) | 45477 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Negative Sequence Symmetric Voltage.
mPosSeqV/.ValueIntMin | V(Positive Sequence) Magnitude (5-min interval minimum) | 45479 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Posive Sequence Symmetric Voltage.
mPosSeqV/.ValueIntAvg | V(Positive Sequence) Magnitude (5-min interval average) | 45481 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Posive Sequence Symmetric Voltage.
mPosSeqV/.ValueIntMax | V(Positive Sequence) Magnitude (5-min interval maximum) | 45483 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Posive Sequence Symmetric Voltage.
mZeroSeqV/.ValueIntMin | V(Zero Sequence) Magnitude (5-min interval minimum) | 45485 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Zero Sequence Symmetric Voltage.
mZeroSeqV/.ValueIntAvg | V(Zero Sequence) Magnitude (5-min interval average) | 45487 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Zero Sequence Symmetric Voltage.
mZeroSeqV/.ValueIntMax | V(Zero Sequence) Magnitude (5-min interval maximum) | 45489 | No | volts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Zero Sequence Symmetric Voltage.
mPercentUnbalance/.ValueIntMin | Percent Current Unbalance (5-min interval minimum) | 45491 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Phase Unbalance.
mPercentUnbalance/.ValueIntAvg | Percent Current Unbalance (5-min interval average) | 45493 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Phase Unbalance.
mPercentUnbalance/.ValueIntMax | Percent Current Unbalance (5-min interval maximum) | 45495 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Phase Unbalance.
mPercentVoltageUnbalance/.ValueIntMin | Percent Voltage unbalance Negative Sequence (5-min interval minimum) | 45497 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Voltage Unbalance.
mPercentVoltageUnbalance/.ValueIntAvg | Percent Voltage unbalance Negative Sequence (5-min interval average) | 45499 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Voltage Unbalance.
mPercentVoltageUnbalance/.ValueIntMax | Percent Voltage unbalance Negative Sequence (5-min interval maximum) | 45501 | No | percent | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Percent Voltage Unbalance.
mVAA/.ValueIntMin | Apparent Power Phase A (5-min interval minimum) | 45503 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A VA.
mVAA/.ValueIntAvg | Apparent Power Phase A (5-min interval average) | 45505 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A VA.
mVAA/.ValueIntMax | Apparent Power Phase A (5-min interval maximum) | 45507 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A VA.
mVAB/.ValueIntMin | Apparent Power Phase B (5-min interval minimum) | 45509 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B VA.
mVAB/.ValueIntAvg | Apparent Power Phase B (5-min interval average) | 45511 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B VA.
mVAB/.ValueIntMax | Apparent Power Phase B (5-min interval maximum) | 45513 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B VA.
mVAC/.ValueIntMin | Apparent Power Phase C (5-min interval minimum) | 45515 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C VA.
mVAC/.ValueIntAvg | Apparent Power Phase C (5-min interval average) | 45517 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C VA.
mVAC/.ValueIntMax | Apparent Power Phase C (5-min interval maximum) | 45519 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C VA.
mVAtotal/.ValueIntMin | Apparent Power (5-min interval minimum) | 45521 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase VA.
mVAtotal/.ValueIntAvg | Apparent Power (5-min interval average) | 45523 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase VA.
mVAtotal/.ValueIntMax | Apparent Power (5-min interval maximum) | 45525 | No | volt-amperes | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase VA.
mVarA/.ValueIntMin | Reactive Power Phase A (5-min interval minimum) | 45527 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A reactive power.
mVarA/.ValueIntAvg | Reactive Power Phase A (5-min interval average) | 45529 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A reactive power.
mVarA/.ValueIntMax | Reactive Power Phase A (5-min interval maximum) | 45531 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A reactive power.
mVarB/.ValueIntMin | Reactive Power Phase B (5-min interval minimum) | 45533 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B reactive power.
mVarB/.ValueIntAvg | Reactive Power Phase B (5-min interval average) | 45535 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B reactive power.
mVarB/.ValueIntMax | Reactive Power Phase B (5-min interval maximum) | 45537 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B reactive power.
mVarC/.ValueIntMin | Reactive Power Phase C (5-min interval minimum) | 45539 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C reactive power.
mVarC/.ValueIntAvg | Reactive Power Phase C (5-min interval average) | 45541 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C reactive power.
mVarC/.ValueIntMax | Reactive Power Phase C (5-min interval maximum) | 45543 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C reactive power.
mVARtotal/.ValueIntMin | Reactive Power (5-min interval minimum) | 45545 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase reactive power.
mVARtotal/.ValueIntAvg | Reactive Power (5-min interval average) | 45547 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase reactive power.
mVARtotal/.ValueIntMax | Reactive Power (5-min interval maximum) | 45549 | No | volt-amperes-reactive | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase reactive power.
mWA/.ValueIntMin | Real Power Phase A (5-min interval minimum) | 45551 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A real power.
mWA/.ValueIntAvg | Real Power Phase A (5-min interval average) | 45553 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A real power.
mWA/.ValueIntMax | Real Power Phase A (5-min interval maximum) | 45555 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase A real power.
mWB/.ValueIntMin | Real Power Phase B (5-min interval minimum) | 45557 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B real power.
mWB/.ValueIntAvg | Real Power Phase B (5-min interval average) | 45559 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B real power.
mWB/.ValueIntMax | Real Power Phase B (5-min interval maximum) | 45561 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase B real power.
mWC/.ValueIntMin | Real Power Phase C (5-min interval minimum) | 45563 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C real power.
mWC/.ValueIntAvg | Real Power Phase C (5-min interval average) | 45565 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C real power.
mWC/.ValueIntMax | Real Power Phase C (5-min interval maximum) | 45567 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | Phase C real power.
mWtotal/.ValueIntMin | Real Power (5-min interval minimum) | 45569 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase real power.
mWtotal/.ValueIntAvg | Real Power (5-min interval average) | 45571 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase real power.
mWtotal/.ValueIntMax | Real Power (5-min interval maximum) | 45573 | No | watts | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0 |  | 3 Phase real power.
mPFapparentTotalIntegratedDisplay/Value | mPFApparentTotalIntegratedDisplayValue | 45575 | No | no-units | FLOAT | 4 | No |  | No | No |  |  |  |  | No | 0
mReceivedKWHourDispUnit/Value | W-hours Received | 45601 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mKDeliveredWHourDispUnit/Value | W-hours Delivered | 45603 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetEnergyDispUnit/Value | W-hours Net | 45605 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalEnergyDispUnit/Value | W-hours Total | 45607 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLeadingVARhDispUnit/Value | VAR-hours Positive | 45609 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLaggingVARhDispUnit/Value | VAR-hours Negative | 45611 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetVARhDispUnit/Value | VAR-hours Net | 45613 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVARhDispUnit/Value | VAR-hours Total | 45615 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVADispUnit/Value | VA-hours Total | 45617 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mReceivedKWHourADispUnit/Value | W-hours Received Phase A | 45619 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mReceivedKWHourBDispUnit/Value | W-hours Received Phase B | 45621 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mReceivedKWHourCDispUnit/Value | W-hours Received Phase C | 45623 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mOutputKWHourADispUnit/Value | W-hours Delivered Phase A | 45625 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mOutputKWHourBDispUnit/Value | W-hours Delivered Phase B | 45627 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mOutputKWHourCDispUnit/Value | W-hours Delivered Phase C | 45629 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetEnergyADispUnit/Value | W-hours Net Phase A | 45631 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetEnergyBDispUnit/Value | W-hours Net Phase B | 45633 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetEnergyCDispUnit/Value | W-hours Net Phase C | 45635 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalEnergyADispUnit/Value | W-hours Total Phase A | 45637 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalEnergyBDispUnit/Value | W-hours Total Phase B | 45639 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalEnergyCDispUnit/Value | W-hours Total Phase C | 45641 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLeadingVARhADispUnit/Value | VAR-hours Positive Phase A | 45643 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLeadingVARhBDispUnit/Value | VAR-hours Positive Phase B | 45645 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLeadingVARhCDispUnit/Value | VAR-hours Positive Phase C | 45647 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLaggingVARhADispUnit/Value | VAR-hours Negative Phase A | 45649 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLaggingVARhBDispUnit/Value | VAR-hours Negative Phase B | 45651 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mLaggingVARhCDispUnit/Value | VAR-hours Negative Phase C | 45653 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetVARhADispUnit/Value | VAR-hours Net Phase A | 45655 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetVARhBDispUnit/Value | VAR-hours Net Phase B | 45657 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mNetVARhCDispUnit/Value | VAR-hours Net Phase C | 45659 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVARhADispUnit/Value | VAR-hours Total Phase A | 45661 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVARhBDispUnit/Value | VAR-hours Total Phase B | 45663 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVARhCDispUnit/Value | VAR-hours Total Phase C | 45665 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVAADispUnit/Value | VA-hours Phase A | 45667 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVABDispUnit/Value | VA-hours Phase B | 45669 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0
mTotalVACDispUnit/Value | VA-hours Phase C | 45671 | No | no-units | INT | 4 | No |  | No | No |  |  |  |  | No | 0

## Sheet1
VendorName/Value
ModelName/Value
iDisplayName/Value
iDeviceType/Value
SerialNumber/Value
SoftwareVersion/Value
iDeviceVARating/Value
iDeviceVoltsRating/Value
iNumPhases/Value
iFieldReplaceableUnit/Value
iNominalFrequency/Value
iDeviceAmpsRating/Value
sStatus/Value
mACVAB/Value
mACVBC/Value
mACVCA/Value
mACVavgLL/Value
mACVAN/Value
mACVBN/Value
mACVCN/Value
mACVavgLN/Value
mPosSeqV/Value
mNegSeqV/Value
mZeroSeqV/Value